## Sheet1
IFP-1000 Battery Calculation Worksheet
(all currents stated in mA)
2026-07-29
Instructions: fill in shaded data fields
Device | Quantity of | Standby mA | Alarm mA | Total Device | Total Device
Description | Devices | Per Device | Per Device | Standby mA | Alarm mA
IFP-1000 Fire Alarm Control Panel | 1 | 140 | 260 | 140 | 260
SLC Devices (1,016 Max.) | 6 | 0.55 | 0.55 | 3.3 | 3.3
5815XL SLC Expanders (7 Max.) | 0 | 55 | 55 | 0 | 0
RA-1000 Remote Annunciator (8 Max.) | 0 | 20 | 25 | 0 | 0
5824 Serial/Parallel Module (2 Max.) | 0 | 45 | 45 | 0 | 0
RPS-1000 Remote Power Supply | 0 | 10 | 10 | 0 | 0
5865-4/5865-3 LED Annunciator (5865 plus | 0 | 35 | 145 | 0 | 0
5880 LED Driver Module 5880 = 8 Max.) | 0 | 35 | 200 | 0 | 0
Total 5820 System Current |  |  |  | 143.3 | 263.3
Auxilliary Devices (list all)
4-wire duct detector | 0 |  |  | 0 | 0
4-wire beam detector | 0 |  |  | 0 | 0
door holder | 0 |  | N/A * | 0 | #VALUE!
EOL relay | 0 |  |  | 0 | 0
Smoke Detector | 0 |  |  | 0 | 0
Heat Detector | 0 |  |  | #VALUE! | #VALUE!
Auxilliary Device Totals | 0 |  |  | #VALUE! | #VALUE!
Notification Appliances (list all)
ADA strobes 15cd | 4 | N/A | 47 | N/A | 188
ADA strobes 110cd | 0 | N/A | 0 | N/A | 0
Horn/Strobes 15cd | 4 | N/A | 77 | N/A | 308
Horn/Strobes 30cd | 1 | N/A | 87 | N/A | 87
Horn/Strobes 110cd | 1 | N/A | 140 | N/A | 140
Horns | 0 | N/A | 0 | N/A | 0
Notification Appliance Totals | 10 |  |  | N/A | 723
Summary Section
Standby Hrs. Required | 24
Alarm Sounding Minutes | 5
Total System Standby mA | #VALUE!
Total System Alarm mA | #VALUE!
Total System Standby A/H | #VALUE!
Total System Alarm A/H | #VALUE!
Min. A/H Battery Required | #VALUE! | #VALUE!
Recommended A/H Battery ** | #VALUE! | #VALUE!
* If you are using door holders, you do not need to consider door holder current for alarm current, because power is removed during that time.
However, during normal operation, door holders draw current and must be included in the 5.0A total current that can be drawn from the panel.
** Use next size battery with capacity greater than required.

## BldgLoadCalc
BUILDING LOAD CALCULATION
Iceland
Date Printed:
2026-07-29 15:48
BLDG
SF: | 200000
BUILDING AREA | [7 empty] | 200000 | SF
| OFFICE | 200000 | SQ. FT. x | 5% | = | 10000 | sq. ft.
| WAREHOUSE | 200000 | SQ. FT. x | 25% | = | 50000 | sq. ft.
| SHOP AREA | 200000 | SQ. FT. x | 0% | = | 0 | sq. ft.
| RETAIL | 200000 | SQ. FT. x | 0% | = | 0 | sq. ft.
| RESTAURANT | 200000 | SQ. FT. x | 0% | = | 0 | sq. ft.
| KITCHEN | 200000 | SQ. FT. x | 0% | = | 0 | sq. ft.
| FUTURE | 200000 | SQ. FT. x | 70% | = | 140000 | sq. ft.
LIGHTING | [7 empty] | 205000 | VA |  | 246.6907
| OFFICE | 10000 | SQ. FT. x | 3.5 | VA/SF = | 35000 | VA |  |  | 42.1179
| WAREHOUSE | 50000 | SQ. FT. x | 2 | VA/SF = | 100000 | VA |  |  | 120.3369
| SHOP AREA | 0 | SQ. FT. x | 1 | VA/SF = | 0 | VA |  |  | 0
| RETAIL | 0 | SQ. FT. x | 2.5 | VA/SF = | 0 | VA |  |  | 0
| RESTAURANT | 0 | SQ. FT. x | 2 | VA/SF = | 0 | VA |  |  | 0
| KITCHEN | 0 | SQ. FT. x | 2.2 | VA/SF = | 0 | VA |  |  | 0
| FUTURE | 140000 | SQ. FT. x | 0.5 | VA/SF = | 70000 | VA |  |  | 84.2359
POWER | [7 empty] | 115000 | VA |  | 138.3875
| OFFICE | 10000 | SQ. FT. x | 2 | VA/SF = | 20000 | VA |  |  | 24.0674
| WAREHOUSE | 50000 | SQ. FT. x | 0.5 | VA/SF = | 25000 | VA |  |  | 30.0842
| SHOP AREA | 0 | SQ. FT. x | 6 | VA/SF = | 0 | VA |  |  | 0
| RETAIL | 0 | SQ. FT. x | 4 | VA/SF = | 0 | VA |  |  | 0
| RESTAURANT | 0 | SQ. FT. x | 4 | VA/SF = | 0 | VA |  |  | 0
| KITCHEN | 0 | SQ. FT. x | 15 | VA/SF = | 0 | VA |  |  | 0
| FUTURE | 140000 | SQ. FT. x | 0.5 | VA/SF = | 70000 | VA |  |  | 84.2359
MECHANICAL | [7 empty] | 175000 | VA |  | 210.5897
| OFFICE | 10000 | SQ. FT. x | 8 | VA/SF = | 80000 | VA |  |  | 96.2696
| WAREHOUSE | 50000 | SQ. FT. x | 0.5 | VA/SF = | 25000 | VA |  |  | 30.0842
| SHOP AREA | 0 | SQ. FT. x | 0.5 | VA/SF = | 0 | VA |  |  | 0
| RETAIL | 0 | SQ. FT. x | 12 | VA/SF = | 0 | VA |  |  | 0
| RESTAURANT | 0 | SQ. FT. x | 12 | VA/SF = | 0 | VA |  |  | 0
| KITCHEN | 0 | SQ. FT. x | 15 | VA/SF = | 0 | VA |  |  | 0
| FUTURE | 140000 | SQ. FT. x | 0.5 | VA/SF = | 70000 | VA |  |  | 84.2359
EQUIPMENT | [7 empty] | 105000 | VA |  | 126.3538
| OFFICE | 10000 | SQ. FT. x | 1 | VA/SF = | 10000 | VA |  |  | 12.0337
| WAREHOUSE | 50000 | SQ. FT. x | 0.5 | VA/SF = | 25000 | VA |  |  | 30.0842
| SHOP AREA | 0 | SQ. FT. x | 4 | VA/SF = | 0 | VA |  |  | 0
| RETAIL | 0 | SQ. FT. x | 2 | VA/SF = | 0 | VA |  |  | 0
| RESTAURANT | 0 | SQ. FT. x | 5 | VA/SF = | 0 | VA |  |  | 0
| KITCHEN | 0 | SQ. FT. x | 50 | VA/SF = | 0 | VA |  |  | 0
| FUTURE | 140000 | SQ. FT. x | 0.5 | VA/SF = | 70000 | VA |  |  | 84.2359
BATTERY CHARGERS | [7 empty] | 0 | VA |  | 0
|  | 0 | EACH x | 10000 | VA/EACH = | 0 | VA |  |  | 0
SITE LIGHTING | [7 empty] | 0 | VA |  | 0
| WALLPACK | 0 | EACH x | 455 | VA/EACH = | 0 | VA |  |  | 0
| POLE FIXTURES | 0 | EACH x | 455 | VA/EACH = | 0 | VA |  |  | 0
| WALKWAY FIXTURES | 0 | EACH x | 205 | VA/EACH = | 0 | VA |  |  | 0
[6 empty] | = |  | = |  | = | =
|  |  |  | TOTAL VA = |  | 600000 | VA | 600000 | VA | 722.0217 | 722.0217
|  | 600000 | VA/ | 831 | = | 722.0217 | Amps
120/208V USE 360
277/480V USE 831
|  | WATTS/SF = | 3
Expected Watts/SF per Rick Cerato of SMUD 8/97
| Unconditioned Warehouse w/small office |  | 2 | watts/sf
| Conditioned Office |  | 4 to 7 | watts/sf
| Manufacturing Facility |  | 10 | watts/sf
Mark III Office Bldg
110kW Peak Demand (306amps 208V 3PH)
20,000 sf office
5.5 watts/sf

## Load Calc
LOAD CALCULATION |  |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Iceland |  |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[5 empty] | Stinger Leg | Stinger Leg | Stinger Leg
Total | Load |  |  |  | Panel 1 | Panel 2 | Panel 3 | Panel 4 | Panel 5 | Panel 6 | Panel 7 | Panel 8 | Panel 9 | Panel 10 | Panel 11 | Panel 12 | Panel 13 | Panel 14 | Panel 15 | Panel 16 | Panel 17 | Panel 18 | Panel 19 | Panel 20
Load | Description |  |  |  | Stinger Leg Panel 1: SE PANEL; Stinger Leg Panel 2: SW PANEL; Stinger Leg Panel 3: NE PANEL
21.2 | kVA Continuous Non-Motor |  |  |  | 17.9 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | kVA 25% Continuous Non-Motor |  |  |  | 4.475 | 0 | 0.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | kVA Non-Continuous |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | kVA Receptacle (First 10KVA) |  |  |  | 7.2 | 4.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | kVA Receptacle(Balance at 50%) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7 | kVA Motor Loads |  |  |  | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#VALUE! | kVA 25% of Largest Motor |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#N/A | kVA Kitchen Equipment |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | kVA Hotel/Motel Demand (NEC 220-11) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
= | bar: Stinger Leg Panel 1 to Stinger Leg Panel 20
#VALUE! | Load kVA (Per NEC) |  |  | Pnl kVA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | Amps at 480 Volt 3 Phase |  |  | Pnl Amps | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | Amps at 208 Volt 3 Phase |  |  | Allowed Load | 200 | 125 | 125 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999 | 99999
#VALUE! | Amps at 240 Volt 3 Phase |  |  | % Phase Imbal 3 ph | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | Amps at 240 Volt 1 Phase |  |  | Phase A Amps 3 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | * Load kVA 100% Rated Breaker |  |  | Phase B Amps 3 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | * Amps at 480 Volt 3 Phase 100% Rated Breaker |  |  | Phase C Amps 3 ph ** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | * Amps at 208 Volt 3 Phase 100% Rated Breaker |  |  | Avg Amps 3 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
** No diversity taken; feed through panels assumed balanced
* Per NEC 220-10(b) Exception: "Where the assembly including the overcurrent
devices protecting the feeder(s) are listed for operation at 100 percent of their
| rating, neither the ampere rating of the overcurrent device nor the ampacity of |  |  |  | Stinger Leg Panel 2: COMPLETED thru panel 6
the feeder conductors shall be less than the sum of the continuous load plus
the noncontinuous load."
(i.e. if a 100% rated breaker or fused device is used, the feeder and breaker
can be rated at this lower ampacity)
(Note: 100% rated breakers cost about 10% to 20% more than 80% rated
circuit breakers).
|  |  |  | % Phase Imbal 1 ph | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| * See also NEC sections: |  |  | Phase A Amps 1 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 210-10(b) exception |  |  | Phase B Amps 1 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 210-22(c) exception |  |  | Avg Amps 1 ph** | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 220-3(a) exception |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 384-16(c) exception |  |  | ** No diversity taken; feed through panels assumed balanced
422-4(a) exception #2
422-14(b) FPN
424-3
LOAD CALCULATION
NEC 220-35 Optional Calculations for Additional Loads to Existing Installations |  |  |  |  | Stinger Leg Panel 2: HOTEL/MOTEL CALCULATIONS (NEC 220-11)
[6 empty] | 0 | kVA Without Demand Factors Applied
Total | Load
Load | Description |  |  |  | Stinger Leg Panel 2: 0; Stinger Leg Panel 3: kVA First 20,000 VA AT 50% Demand Factor
90 | kVA Maximum demand for 12 month period from 2-96 to 1-97 |  |  |  | Stinger Leg Panel 2: 0; Stinger Leg Panel 3: kVA 20,001 to 100,000 VA AT 40% Demand Factor
| Based on Maximum demand shown on Utility Bills |  |  |  | Stinger Leg Panel 2: 0; Stinger Leg Panel 3: kVA Over 100,000VA at 30% Demand Factor
[6 empty] | 0 | kVA After Demand Factors Applied
22.5 | kVA 25% of Maximum demand
200 | kVA Proposed Additional Load
========= | ==============================================
312.5 | kVA Total Load
375.8791 | Amps at 480 Volt 3 Phase
867.4133 | Amps at 208 Volt 3 Phase
751.7582 | Amps at 240 Volt 3 Phase
1302.0833 | Amps at 240 Volt 1 Phase
0 | Amps Service Size
Total | Load Per
Amps | NEC 220-32(c)
100.725 | Panel 3CA | 5 | Units Factor | 0.45
| 6360 | SF at 3VA/SF for Ltg/Receptacles |  | 19080 | bar: Stinger Leg Panel 1
Largest of Heating or AC
| 5 | AC Units at 790VA/Each |  | 0 | Stinger Leg Panel 1: VA; Stinger Leg Panel 2: 3950; Stinger Leg Panel 3: VA
| 5 | Heating Units at 1300VA/Each |  | 6500 | Stinger Leg Panel 1: VA; Stinger Leg Panel 2: 6500; Stinger Leg Panel 3: VA
| Appliance Branch Ckts (1,500VA x 2/Unit) |  |  | 15000 | bar: Stinger Leg Panel 1
| Virtual Cooking (8,000W/Unit) |  |  | 40000 | bar: Stinger Leg Panel 1
==========
80580 | bar: Stinger Leg Panel 1
Apartment Units
200 | SF Studio
(1) 1500 VA/appliance branch ckt (NEC 220-16)
(2) 3VA/SF for general ltg and general use receptacles (NEC 220-3b)
LOAD CALCULATION
Total | Load
Load | Description
#VALUE! | kVA Panel | SE PANEL
#VALUE! | kVA Panel | SW PANEL
#VALUE! | kVA Panel | NE PANEL
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
#VALUE! | kVA Panel
=
#VALUE! | Load kVA
#VALUE! | Amps at 480 Volt 3 Phase
#VALUE! | Amps at 208 Volt 3 Phase
Iceland
Predicted Actual Load |  |  | Demand Factor | kVA Demand Load
21.2 | kVA Continuous Non-Motor |  | 0.9 | 19.08
0 | kVA Non-Continuous |  | 0.5 | 0
10 | kVA Receptacle (First 10KVA) |  | 0.5 | 5
3.4 | kVA Receptacle(Balance at 50%) |  | 0.5 | 1.7
0.7 | kVA Motor Loads |  | 0.5 | 0.35
#N/A | kVA Kitchen Equipment |  | 1 | #N/A
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | 1 | 0
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | 0.5 | #VALUE!
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | 0.5 | #VALUE!
#N/A | Total kVA Connected |  | Total kVA Demand Predicted | #N/A
#N/A | Amps at 480V 3 Ph |  | Total Amps Demand Predicted | #N/A

## FirePumpCalcs
FIRE PUMP CONDUCTOR CALCULATIONS
FIRE PUMP | 150 | HP | 180.8333 | Amps 480V 3 Phase
JOCKEY PUMP | 2 | HP | 3.4 | Amps 480V 3 Phase
HEATER | 10 | kVA | 12.0482 | Amps 480V 3 Phase
LIGHTS/MISC. | 1 | kVA | 1.2048 | Amps 480V 3 Phase
=
SUBTOTAL |  |  | 197.4863 | Amps 480V 3 Phase
25% OF LARGEST MOTOR |  |  | 45.2083 | Amps 480V 3 Phase
25% LCL |  |  | 3.3133 | Amps 480V 3 Phase
=
TOTAL |  |  | 246.0079 | Amps 480V 3 Phase
NOTE TO UTILITY COMPANY
Transformer protection must not trip and voltage must not drop more than 14% (15% at pump controller)
when fire pump and jockey pump are in locked rotor condition and all building loads are on(NEC 695-8(e)).
Anticipated loads are:
FIRE PUMP LRA | 150 | HP | 1085 | Amps 480V 3 Phase
JOCKEY PUMP LRA | 2 | HP | 20.4 | Amps 480V 3 Phase
HEATER | 10 | kVA | 12.0482 | Amps 480V 3 Phase
LIGHTS/MISC. | 1 | kVA | 1.2048 | Amps 480V 3 Phase
=
TOTAL |  |  | 1118.653 | Amps 480V 3 Phase
NOTE TO UTILITY COMPANY
Transformer protection must not trip and voltage must not drop more than 14% (15% at pump controller)
when fire pump and jockey pump are in locked rotor condition and all building loads are on(NEC 695-8(e)).
Anticipated loads are:
FIRE PUMP LRA | 150 | HP | 1085 | Amps 480V 3 Phase
JOCKEY PUMP LRA | 2 | HP | 20.4 | Amps 480V 3 Phase
Max. Bldg Load |  |  | As Determined by Utility Company
FIRE PUMP VOLTAGE DROP CALCULATIONS
NEC 695-8(e)
620 | LF Feeder
Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[7 empty] | 335600 | Circ Mills
77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
2.897% | %VD @ 115% OF FLA 5% Limit | [5 empty] | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
13.17% | %VD @ LRA 15% limit | [5 empty] | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
FLA Calculation
[5 empty] | 246.0079 | Amps
[5 empty] | % Voltage Drop |  | Volts Dropped
[5 empty] | 77 F | 167F | 77 F | 167F
[5 empty] | 2.897% | 3.447% | 13.9072 | 16.5432
LRA Calculation
[5 empty] | 1118.653 | Amps
[5 empty] | % Voltage Drop |  | Volts Dropped
[5 empty] | 77 F | 167F | 77 F | 167F
[5 empty] | 13.17% | 15.67% | 63.2392 | 75.2257
| NFPA TABLE 6-5.1.1 |  | 1/6 of LRA
HP | LRA | Code Letter | FLA
5 | 46 | J | 7.6667
7.5 | 64 | H | 10.6667
10 | 81 | H | 13.5
15 | 116 | G | 19.3333
20 | 145 | G | 24.1667
25 | 183 | G | 30.5
30 | 217 | G | 36.1667
40 | 290 | G | 48.3333
50 | 362 | G | 60.3333
60 | 435 | G | 72.5
75 | 543 | G | 90.5
100 | 725 | G | 120.8333
125 | 908 | G | 151.3333
150 | 1085 | G | 180.8333
200 | 1450 | G | 241.6667
250 | 1825 | G | 304.1667
300 | 2200 | G | 366.6667
350 | 2550 | G | 425
400 | 2900 | G | 483.3333
450 | 3250 | G | 541.6667
500 | 3625 | G | 604.1667
2 | 20.4 | G | 3.4

## Tables (hidden)
NEC TABLE 220-32 1993
Optional Calculation - Demand Factors for
Three or More Multifamily Dwelling Units
Number of
Dwelling | Demand
Units | Factor
0 | 1
1 | 1
2 | 1
3 | 0.45
4 | 0.45
5 | 0.45
6 | 0.44
7 | 0.44
8 | 0.43
9 | 0.43
10 | 0.43
11 | 0.42
12 | 0.42
13 | 0.41
14 | 0.4
15 | 0.39
16 | 0.39
17 | 0.39
18 | 0.38
19 | 0.38
20 | 0.38
21 | 0.37
22 | 0.36
23 | 0.36
24 | 0.35
25 | 0.35
26 | 0.34
27 | 0.34
28 | 0.33
29 | 0.33
30 | 0.33
31 | 0.32
32 | 0.31
33 | 0.31
34 | 0.3
35 | 0.3
36 | 0.3
37 | 0.29
38 | 0.29
39 | 0.28
40 | 0.28
41 | 0.28
42 | 0.28
43 | 0.27
44 | 0.27
45 | 0.27
46 | 0.26
47 | 0.26
48 | 0.26
49 | 0.26
50 | 0.26
51 | 0.25
52 | 0.25
53 | 0.25
54 | 0.25
55 | 0.25
56 | 0.24
57 | 0.24
58 | 0.24
59 | 0.24
60 | 0.24
61 | 0.24
62 | 0.23
63 | 0.23
64 | 0.23

## DesignChecklist
Design Check List
Drawings Setup
Utility Transformer Located
Drawings Sent to Electric Utility for markup
Drawings Sent to Telephone Utility for markup
Conditions of Approval Received (site ltg req'mts)
Site Photometric Completed
Interior Photometric Completed
Exterior Lighting Control Diagram(s)
Fire Pump located
Fire Risers Located
Fire Bells Located
PIV located
Landscape Controller
MSB located
Telephone Located
North Arrow
Vicinty Map
Fixture Schedule
Title 24 Mandatory Notes
Title 24 Ltg 1, Ltg 2
Title 24 Ltg 3 (if credits taken)
Lighting Plan
Title 24 sweep off control diagram
Single Line Diagram
Panel Schedules
Power Plan
HVAC units shown
HVAC roof receptacles shown (GFI/WP)
Water Heaters
Sump Pumps
Starters
Evap Cooler Schematic(s)
Exh Fans
Transformer weight on second floor (especially K13/K4)
Protective bollards around transformers/panels/MSB
Neutrals/harmonics/oversized panel & feeder neutrals
Voltage drop
450-21 12" Clearance GE placarded for less 450-9 exception
450-21 larger than 112.5kva shall be in fire resistive transformer room
450-42 Walls, floor and roof 3 hour construction! 1hour permitted if sprinklered
384-4 No piping, ducts or equipment foreign to the electrical in elect room

## ToDo (hidden)
Fix panel 7 - does not print properly - printed OK at FC house Jan 11 1998 - Check at Mark III
Add warning to load calc page for voltage drop and AIC exceeded
Add voltage drop calc for 100% of allowable load
Add voltage drop calc for 80% of allowable load
Find way to show summary of links
Password protection and selection of sheets depending on user
TEST ARC WELDER
TEST RESISTANCE WELDER
TEST VOLTAGE DROP CALC
TEST SHORT CIRCUIT CALC
Modify pulldowns to allow for added pulldowns on individual projects
DONE
Set print areas 13 to 20
Add welders (Arc and Resistance) to all panels - requires adding 2 lines in schedule
Add Panels 13 to 20
Add 13 to 20 to Index
Change Pulldown menu's panels 13 to 20
Add 13 to 20 to Load Calc
Add voltage drop calculator
Add short circuit calculator

## SE Panel
|  |  | 99999 | kVA Limitation | [6 empty] | 200 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
| WARNING |  | ALLOWED LOAD: | [6 empty] | #VALUE! |  |  |  | % PHASE IMBALANCE | 99999 | AIC @ Source
| Stinger Leg PH B |  | 200 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 500 | LF Feeder
PANEL: | SE PANEL | [16 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 167800 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
NE PANEL |  | C | 4.3 | 60/ | 1 | A |  |  | 2 | 20/1 | 0.3 | C | PERIMETER LIGHT 1 |  | #VALUE! | %VD @ Panel NEC Calc |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
NE PANEL |  | C | CB: /; NO: 3; B: B; NO: 4; CB: PFB |  | Spare |  | 5.537% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
NE PANEL |  | C | 3.8 | 3 | 5 |  |  | C | 6 | 20/1 | 0.3 | C | PERIMETER LIGHT 2 |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
SW PANEL |  | C | 3.1 | 60/ | 7 | A |  |  | 8 | 20/1 | 1.2 | R | EXTERIOR RECEPTACLE 1
SW PANEL |  | C | CB: /; NO: 9; B: B; NO: 10; CB: PFB |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
SW PANEL |  | C | 2.4 | 3 | 11 |  |  | C | 12 | 20/1 | 1.2 | R | EXTERIOR RECEPTACLE 2 |  | 225 | kVA |  |  |  | #VALUE! | Amps
FLOOD LIGHT 1 |  | C | 1.3 | 20/1 | 13 | A |  |  | 14 | PFB |  |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Space |  |  | CB: PFB; NO: 15; B: B; NO: 16; CB: PFB |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
FLOOD LIGHT 2 |  | C | 1.3 | 20/1 | 17 |  |  | C | 18 | PFB |  |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
EMERGENCY LIGHTS |  | C | 1.1 | 20/1 | 19 | A |  |  | 20 | PFB |  |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Space |  |  | CB: PFB; NO: 21; B: B; NO: 22; CB: PFB |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
UTILITY RECEPTACLE 1 |  | R | 1.2 | 20/1 | 23 |  |  | C | 24 | PFB |  |  | Spare | [6 empty] | #N/A | Amps |  |  | 200 | Amps
UTILITY RECEPTACLE 2 |  | R | 1.2 | 20/1 | 25 | A |  |  | 26 | PFB |  |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Space |  |  | CB: PFB; NO: 27; B: B; NO: 28; CB: PFB |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
UTILITY RECEPTACLE 3 |  | R | 1.2 | 20/1 | 29 |  |  | C | 30 | PFB |  |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 4.643% | 5.537% | 11.1442 | 13.2896
UTILITY RECEPTACLE 4 |  | R | 1.2 | 20/1 | 31 | A |  |  | 32 | PFB |  |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
17.9 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 240 | Line to Line Voltage "V"
4.475 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 3/0 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 3 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
7.2 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
4.475 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
|  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
0 |  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
16.11 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
3.6 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W

## SW Panel
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
| WARNING |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
| Stinger Leg PH B |  | 125 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | SW PANEL | [16 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 26240 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
UTILITY RECEPTACLE 1 |  | R | 1.2 | 20/1 | 1 | A |  |  | 2 | PFB |  |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: PFB; NO: 3; B: B; NO: 4; CB: PFB |  | Spare |  | 4426% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
UTILITY RECEPTACLE 2 |  | R | 1.2 | 20/1 | 5 |  |  | C | 6 | PFB |  |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
UTILITY RECEPTACLE 3 |  | R | 1.2 | 20/1 | 7 | A |  |  | 8 | PFB |  |  | Spare
Spare |  |  | CB: PFB; NO: 9; B: B; NO: 10; CB: PFB |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
UTILITY RECEPTACLE 4 |  | R | 1.2 | 20/1 | 11 |  |  | C | 12 | PFB |  |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
SUMP PUMP |  | M | 0.7 | 20/1 | 13 | A |  |  | 14 | PFB |  |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: PFB; NO: 15; B: B; NO: 16; CB: PFB |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: PFB; NO: 17; C: C; NO: 18; CB: PFB |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: PFB; NO: 19; A: A; NO: 20; CB: PFB |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: PFB; NO: 21; B: B; NO: 22; CB: PFB |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: PFB; NO: 23; C: C; NO: 24; CB: PFB |  | Spare | [6 empty] | #N/A | Amps |  |  | 125 | Amps
Spare |  |  | CB: PFB; NO: 25; A: A; NO: 26; CB: PFB |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: PFB; NO: 27; B: B; NO: 28; CB: PFB |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: PFB; NO: 29; C: C; NO: 30; CB: PFB |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 3712% | 4426% | 8908.0664 | 10622.9883
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 0.7 | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 0.6 | 0.78
[15 empty] | 0.5 | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 0.4 | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 0.3 | 0.55 |  |  |  | 240 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 0.2 | 0.45 |  |  |  | 6 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 5 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
4.8 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0.7 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
2.4 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0.35 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W

## NE Panel
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
| WARNING |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
| Stinger Leg PH B |  | 125 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | NE PANEL | [16 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
NEON SIGN 1 |  | C | 1.4 | 20/1 | 1 | A |  |  | 2 | 20/1 | 1.2 | R | UTILITY RECEPTACLE 1 |  | #VALUE! | %VD @ Panel NEC |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: PFB; NO: 3; B: B; NO: 4; CB: PFB |  | Spare |  | 758.3% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
NEON SIGN 2 |  | C | 1.4 | 20/1 | 5 |  |  | C | 6 | 20/1 | 1.2 | R | UTILITY RECEPTACLE 2 |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
LED SIGNS |  | C | 0.5 | 20/1 | 7 | A |  |  | 8 | 20/1 | 1.2 | R | UTILITY RECEPTACLE 3
Spare |  |  | CB: PFB; NO: 9; B: B; NO: 10; CB: PFB |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  |  | PFB | 11 |  |  | C | 12 | 20/1 | 1.2 | R | UTILITY RECEPTACLE 4 |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: PFB; NO: 13; A: A; NO: 14; CB: PFB |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: PFB; NO: 15; B: B; NO: 16; CB: PFB |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: PFB; NO: 17; C: C; NO: 18; CB: PFB |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: PFB; NO: 19; A: A; NO: 20; CB: PFB |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: PFB; NO: 21; B: B; NO: 22; CB: PFB |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: PFB; NO: 23; C: C; NO: 24; CB: PFB |  | Spare | [6 empty] | #N/A | Amps |  |  | 125 | Amps
Spare |  |  | CB: PFB; NO: 25; A: A; NO: 26; CB: PFB |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: PFB; NO: 27; B: B; NO: 28; CB: PFB |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: PFB; NO: 29; C: C; NO: 30; CB: PFB |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 637.5% | 758.3% | 1529.9847 | 1819.9818
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
3.3 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 240 | Line to Line Voltage "V"
0.825 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 4 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
4.8 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0.825 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
2.97 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
2.4 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/240V 3P, 4W

## Panel 4
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 4 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 5
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
Panel: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 4 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 6
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 4 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 7
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 26240 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | #VALUE! | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 4085724% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 3426145% | 4085724% | 7126381.8605 | 8498305.6411
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 6 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 5 | Column to use in MenuPullDowns 3PVC-CU 4PVC-AL 5EMT-CU 6EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | Not Available | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | #VALUE! | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | #VALUE! | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | #VALUE! | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 8
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 26240 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 2.3325 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 4085724% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 3426145% | 4085724% | 7126381.8605 | 8498305.6411
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 6 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 8 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 1940 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 42871.8626 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 2.3325e-05 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 2.3325 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 9
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 10
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 11
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 12
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 13
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 14
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 15
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 16
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 105600 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 5.6386 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 1657164% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 1393110% | 1657164% | 2897669.3185 | 3446900.7579
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 1/0 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 4690 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 17733.7769 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 5.6386e-05 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 5.6386 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 17
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 18
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Panel 19
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: <E> = Existing Load |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <F> = Future Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: N = Non-continuous load | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: M = Motor Load | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: K= Kitchen Load (NEC 220-20)
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: H = Hotel/Motel
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: W= Resistance Welders
0 | kVA Subpanel(s) |  | NO: P = Sub-Panel
0 | kVA Thru fed Panel(s)
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## Menu Pull Dns (hidden)
[14 empty] | PVC-Cu | PVC-Al | EMT-Cu | EMT-Al
[9 empty] | Index | Bus Size | Main Breaker Size | Wire Size | Circular Mils | "C" Value | "C" Value | "C" Value | "C" Value | AIC | Conduit | Wire
VOLTAGE: | BUS: | MAIN: | AIC: | MOUNT: | TYPE: | TYPE: | NOTES: | BOTTOM FEED | 1 | 99999 | 99999 | 18 | 1620 | Not Available | Not Available | Not Available | Not Available | 99999999 | Magnetic Conduit | Copper Wire
VOLTAGE: 120/208V,3P,4W | BUS: 100A | MAIN: MLO | AIC: SERIES RATED | MOUNT: SURFACE | TYPE: PANELBOARD | TYPE: NEMA 1 | NOTES: FEED THROUGH LUGS | TOP FEED | 2 | 100 | 99999 | 16 | 2580 | Not Available | Not Available | Not Available | Not Available | 99999999 | Non-Magnetic Conduit | Aluminum Wire
VOLTAGE: 277/480V,3P,4W | BUS: 125A | MAIN: 60A CB | AIC: 10K MINIMUM | MOUNT: FLUSH | TYPE: LOADCENTER | TYPE: NEMA 3R | NOTES: DOUBLE LUGS | BACK FEED | 3 | 125 | 60 | 14 | 4110 | Not Available | Not Available | Not Available | Not Available | 10000
VOLTAGE: 480V,3P,3W | BUS: 200A | MAIN: 100A CB | AIC: 14K MINIMUM | MOUNT: FREE STANDING | TYPE: DISTRIBUTION BOARD | TYPE: NEMA 12 | NOTES: IG BUS |  | 4 | 200 | 100 | 12 | 6530 | Not Available | Not Available | Not Available | Not Available | 14000
VOLTAGE: 120/240V,1P,3W | BUS: 225A | MAIN: 125A CB | AIC: 22K MINIMUM |  | TYPE: MSB | TYPE: DUST TIGHT | NOTES: OVERSIZED NEUTRAL |  | 5 | 225 | 125 | 10 | 10380 | Not Available | Not Available | Not Available | Not Available | 22000
VOLTAGE: 120/240V 3P, 4W | BUS: 400A | MAIN: 150A CB | AIC: 25K MINIMUM |  | TYPE: MCC |  | NOTES: FEED THRU LUGS, IG BUS AND OVERSIZED NEUTRAL |  | 6 | 400 | 150 | 8 | 16510 | Not Available | Not Available | Not Available | Not Available | 25000
VOLTAGE: 240V 3P, 3W | BUS: 600A | MAIN: 200A CB | AIC: 35K MINIMUM |  | TYPE: PNLBD W/DOOR IN DOOR |  | NOTES: IG BUS AND OVERSIZED NEUTRAL |  | 7 | 600 | 200 | 6 | 26240 | 1950 | 1180 | 1940 | 1180 | 35000
| BUS: 800A | MAIN: 225A CB | AIC: 42K MINIMUM |  | TYPE: PNLBD W/DOUBLE HINGE |  | NOTES: FEED THRU LUGS AND IG BUS |  | 8 | 800 | 225 | 4 | 41740 | 3080 | 1870 | 3060 | 1870 | 42000
| BUS: 1000A | MAIN: 400A CB | AIC: 65K MINIMUM |  | TYPE: PLUGIN BUSWAY |  | NOTES: DOUBLE LUGS, IG BUS AND OVERSIZED NEUTRAL |  | 9 | 1000 | 400 | 2 | 66360 | 4830 | 2970 | 4760 | 2960 | 65000
| BUS: 1200A | MAIN: 600A CB | AIC: 100K MINIMUM |  |  |  | NOTES: DOUBLE LUGS AND IG BUS |  | 10 | 1200 | 600 | 1 | 83690 | 6020 | 3750 | 5880 | 3720 | 100000
| BUS: 1600A | MAIN: 800A CB |  |  |  |  | NOTES: EXISTING PANEL |  | 11 | 1600 | 800 | 1/0 | 105600 | 7460 | 4690 | 7190 | 4670
| BUS: 2000A | MAIN: 1000A CB |  |  |  |  | NOTES: QUAD LUGS |  | 12 | 2000 | 1000 | 2/0 | 133100 | 9090 | 5880 | 8700 | 5800
| BUS: 2500A | MAIN: 1200A CB |  |  |  |  | NOTES: DOUBLE LUGS AND DBL THRU FEED LUGS |  | 13 | 2500 | 1200 | 3/0 | 167800 | 11500 | 7300 | 10400 | 7190
| BUS: 3000A | MAIN: 1600A CB | [6 empty] | 14 | 4000 | 1600 | 4/0 | 211600 | 13400 | 9170 | 12300 | 8850
| BUS: 4000A | MAIN: 2000A CB | [6 empty] | 15 |  | 2000 | 250 | 250000 | 14900 | 10600 | 13500 | 10300
|  | MAIN: 2500A CB | [6 empty] | 16 |  | 2500 | 350 | 350000 | 18700 | 14200 | 16200 | 13500
|  | MAIN: 3000A CB | [6 empty] | 17 |  | 3000 | 400 | 400000 | 19200 | 15800 | 16500 | 14800
|  | MAIN: 4000A CB | [6 empty] | 18 |  | 4000 | 500 | 500000 | 21500 | 18700 | 18100 | 17200
[9 empty] | 19 |  |  | 600 | 600000 | 22700 | 21000 | 18900 | 18900
[9 empty] | 20 |  |  | 750 | 750000 | 24700 | 24300 | 20200 | 21500
[9 empty] | 21 |  |  | 2-3/0 Per Phase | 335600 | 26800 | 18340 | 24600 | 17700
[9 empty] | 22 |  |  | 2-4/0 Per Phase | 423200 | 29800 | 21200 | 27000 | 20600
[9 empty] | 23 |  |  | 2-250 Per Phase | 500000 | 37400 | 28400 | 32400 | 27000
[9 empty] | 24 |  |  | 2-350 Per Phase | 700000 | 38400 | 31600 | 33000 | 29600
[9 empty] | 25 |  |  | 2-400 Per Phase | 800000 | 43000 | 37400 | 36200 | 34400
[9 empty] | 26 |  |  | 2-500 Per Phase | 1000000 | 45400 | 42000 | 37800 | 37800
[9 empty] | 27 |  |  | 2-750 Per Phase | 1500000 | 49400 | 48600 | 40400 | 43000
[9 empty] | 28 |  |  | 3-250 Per Phase | 750000 | 56100 | 42600 | 48600 | 40500
[9 empty] | 29 |  |  | 3-350 Per Phase | 1050000 | 57600 | 47400 | 49500 | 44400
[9 empty] | 30 |  |  | 3-400 Per Phase | 1200000 | 64500 | 56100 | 54300 | 51600
[9 empty] | 31 |  |  | 3-500 Per Phase | 1500000 | 68100 | 63000 | 56700 | 56700
[9 empty] | 32 |  |  | 3-750 Per Phase | 2250000 | 74100 | 72900 | 60600 | 64500
33
34
35
36
37
38
39
40

## Panel 20
|  |  | 99999 | kVA Limitation | [6 empty] | 99999 | Amp Limitation |  |  | Voltage Drop & AIC Calculator (3 phase only - not accurate for 120/240V Panels)
|  |  | Allowed Load: | [6 empty] | #VALUE! |  |  |  | % Phase Unbalance | 99999 | AIC @ Source
|  |  | 99999 | amps | [6 empty] | #VALUE! |  |  | #VALUE! | 99999 | LF Feeder
PANEL: | [17 empty] | Voltage Drop Formula : Factor (21.6 or other) x Distance x Amp Load/Circ Mils
This is a rough order of magnitude calculation only.
[12 empty] | Print Date: |  | 2026-07-29 15:48 |  |  |  | 250000 | Circ Mills
LOAD |  |  | KVA | CB | NO | A | B | C | NO | CB | KVA |  | LOAD |  | 12.743 | AIC @ Panel |  | 77 deg. F - copper use 18.7 for 3 phase in formula and 21.6 for single phase
Spare |  |  | CB: 20/1; NO: 1; A: A; NO: 2; CB: 20/1 |  | Spare |  | #VALUE! | %VD @ Panel |  | 77 deg. F - aluminum use 30.6 for 3 phase in formula and 35.4 for single phase
Spare |  |  | CB: 20/1; NO: 3; B: B; NO: 4; CB: 20/1 |  | Spare |  | 699986% | %VD @ Panel Full Load |  | 167 deg. F - copper use 22.3 for 3 phase in formula and 25.8 for single phase
Spare |  |  | CB: 20/1; NO: 5; C: C; NO: 6; CB: 20/1 |  | Spare |  | #N/A | %VD @ Panel Predicted |  | 167 deg. F - aluminum use 36.7 for 3 phase in formula and 42.4 for single phase
Spare |  |  | CB: 20/1; NO: 7; A: A; NO: 8; CB: 20/1 |  | Spare
Spare |  |  | CB: 20/1; NO: 9; B: B; NO: 10; CB: 20/1 |  | Spare |  | Transformer Max. Short Circuit Let thru with infinite primary |  |  |  |  | NEC Calcuated Load
Spare |  |  | CB: 20/1; NO: 11; C: C; NO: 12; CB: 20/1 |  | Spare |  | 225 | kVA |  |  |  | #VALUE! | Amps
Spare |  |  | CB: 20/1; NO: 13; A: A; NO: 14; CB: 20/1 |  | Spare |  | 208 | Secondary Line to Line Voltage |  |  |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 15; B: B; NO: 16; CB: 20/1 |  | Spare |  | 6.4 | %Z |  |  |  | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 17; C: C; NO: 18; CB: 20/1 |  | Spare |  | 9758.3992 | Secondary AIC Max. |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Spare |  |  | CB: 20/1; NO: 19; A: A; NO: 20; CB: 20/1 |  | Spare |  |  | (75kVA x 1000) / (208V * 1.732) / (5.75% Z) * 100
Spare |  |  | CB: 20/1; NO: 21; B: B; NO: 22; CB: 20/1 |  | Spare | [6 empty] | Predicted Actual Load |  |  |  | 100% of Allowed Load
Spare |  |  | CB: 20/1; NO: 23; C: C; NO: 24; CB: 20/1 |  | Spare | [6 empty] | #N/A | Amps |  |  | 99999 | Amps
Spare |  |  | CB: 20/1; NO: 25; A: A; NO: 26; CB: 20/1 |  | Spare | [6 empty] | % Voltage Drop |  | Volts Dropped |  | % Voltage Drop |  | Volts Dropped
Spare |  |  | CB: 20/1; NO: 27; B: B; NO: 28; CB: 20/1 |  | Spare | [6 empty] | 77 F | 167F | 77 F | 167F | 77 F | 167F | 77 F | 167F
Spare |  |  | CB: 20/1; NO: 29; C: C; NO: 30; CB: 20/1 |  | Spare | [6 empty] | #N/A | #N/A | #N/A | #N/A | 588450% | 699986% | 1223975.5201 | 1455970.8801
Space |  |  | CB: PFB; NO: 31; A: A; NO: 32; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 33; B: B; NO: 34; CB: PFB |  | Space
Space |  |  | CB: PFB; NO: 35; C: C; NO: 36; CB: PFB |  | Space | [6 empty] | 75 deg C is 167 deg F
Space |  |  | CB: PFB; NO: 37; A: A; NO: 38; CB: PFB |  | Space |  | Welder Duty Cycle NEC 630-11b |  |  |  |  | 60 deg C is 140 deg F
Space |  |  | CB: PFB; NO: 39; B: B; NO: 40; CB: PFB |  | Space |  | 70% | 0.84
Space |  |  | CB: PFB; NO: 41; C: C; NO: 42; CB: PFB |  | Space |  | 60% | 0.78
[15 empty] | 50% | 0.71
LOAD CALCULATIONS: |  |  | NO: LEGEND |  |  |  | 40% | 0.63 |  |  |  | AIC Calculations
0 | kVA Continuous Non-Motor |  | NO: L = Provide Lockoff |  |  |  | 30% | 0.55 |  |  |  | 208 | Line to Line Voltage "V"
0 | kVA 25% Continuous Non-Motor |  | NO: PFB = Provision for Future Breaker |  |  |  | 20% | 0.45 |  |  |  | 250 | Wire Size
0 | kVA Non-Continuous |  | NO: <E> = Existing Load | [8 empty] | 7 | Column to use in MenuPullDowns 6PVC-CU 7PVC-AL 8EMT-CU 9EMT-AL
0 | kVA Receptacle (First 10KVA NEC 220-13) |  | NO: <F> = Future Load | [8 empty] | 10600 | "C" value from table
0 | kVA Receptacle(Balance at 50%) |  | NO: C = Continuous Load (>3 hrs per NEC 100) | [8 empty] | 7846.3598 | "f" three phase |  | 1.73 x L x I / ( C x V)
0 | kVA Motor Loads (NEC 430) |  | NO: N = Non-continuous load | [8 empty] | 0.00012743 | "M" |  | 1 / (1 + f)
#VALUE! | kVA 25% of Largest Motor |  | NO: R = Receptacle Load (taken at 180 VA only) | [8 empty] | 12.743 | AIC at Node |  | "Source AIC" x M
#N/A | #VALUE! |  | NO: M = Motor Load
0 | kVA Hotel/Motel Demand (NEC 220-11) |  | NO: K= Kitchen Load (NEC 220-20)
#VALUE! | kVA Arc Welders (NEC 630-11b,21b FPN) |  | NO: H = Hotel/Motel
#VALUE! | kVA Resistance Welders (NEC 630-31b) |  | NO: A= Arc Welders (MG, AC xfmr, DC rectifier)
0 | kVA Subpanel(s) |  | NO: W= Resistance Welders
0 | kVA Thru fed Panel(s) |  | NO: P = Sub-Panel
#VALUE! | Total kVA |  | KVA: #VALUE!; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W |  | Iceland
MAIN SIZED AT 100% (NEC 220-10(b) exception |  |  | KVA: KITCHEN LOAD CALCULATIONS (NEC 220-20) |  |  |  |  | HOTEL/MOTEL CALCULATIONS (NEC 220-11)
#VALUE! | Total kVA (from above) |  | KVA: #VALUE! | kVA Kitchen largest load |  |  |  | 0 | kVA First 20,000 VA AT 50% Demand Factor
0 | Less 25% Continuous Non-Motor (from above) |  | KVA: #VALUE! | kVA Kitchen 2nd largest load |  |  |  | 0 | kVA 20,001 to 100,000 VA AT 40% Demand Factor
#VALUE! | kVA for 100% Rated Main |  | KVA: #VALUE! | Quantity of Kitchen Equipment |  |  |  | 0 | kVA Over 100,000VA at 30% Demand Factor
#VALUE! | (minimum) AMP RATING for 100% Rated Main |  | KVA: #N/A | Demand per NEC Tbl 220-20 |  |  |  | 0 | kVA After Demand Factors Applied
ADDITIONAL CODE REFERENCES |  |  | KVA: 0 | kVA Load w/out demand factor |  |  |  | 0 | kVA Without Demand Factors Applied
210-22(c) exception |  | 422-4(a) exception #2 | KVA: #N/A | kVA Load w/demand factor
220-3(a) exception |  | 422-14(b) FPN | KVA: #VALUE! | kVA Sum of Largest two loads
384(c) exception |  | 424-3 | KVA: #N/A | kVA Kitchen Load per NEC 220-20
|  |  | KVA: ARC WELDER LOAD CALCULATIONS |  |  |  |  | RESISTANCE WELDER LOAD CALCULATIONS
|  |  | KVA: (NEC 630-11b FPN and 630-21b FPN) |  |  |  |  | (NEC 630-31b)
0 |  |  | KVA: 0 | kVA Total Arc Welder loads |  |  |  | 0 | kVA Total Resistance Welder loads
|  |  | KVA: #VALUE! | kVA largest Arc Welder @100% |  |  |  | #VALUE! | kVA largest Resistance Welder @100%
|  |  | KVA: #VALUE! | kVA 2nd largest Arc Welder @100% |  |  |  | #VALUE! | kVA 2nd largest Resistance Welder @60%
Predicted Actual Load |  |  | KVA: #VALUE! | kVA 3rd largest Arc Welder @85% |  |  |  | #VALUE! | kVA Remaing Resistance Welders @60%
0 | kVA Continuous Non-Motor @90% |  | KVA: #VALUE! | kVA 4th largest Arc Welder @70% |  |  |  | #VALUE! | kVA Resistance Welder Loads @% Above
0 | kVA Non-Continuous @50% |  | KVA: #VALUE! | kVA Remaing Arc Welders @60%
0 | kVA Receptacle (First 10KVA) @50% |  | KVA: #VALUE! | kVA Arc Weld Load @% Above
0 | kVA Receptacle(Balance at 25%)
0 | kVA Motor Loads @50%
#N/A | #VALUE!
0 | kVA Hotel/Motel Demand
#VALUE! | kVA Arc Welders @50%
#VALUE! | kVA Resistance Welders @50%
0 | kVA Subpanel(s) @50%
0 | kVA Thru fed Panel(s) @50%
#N/A | Total kVA |  | KVA: #N/A; CB: Amps at; A: VOLTAGE: 120/208V,3P,4W

## FdrSch
FEEDER SCHEDULE
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity |  | Minimum | Comments
A104 | 100 | 1-1/2"' | 1-1/2"' | 4 | #1/0 Al | 100 | 1 | #8 Cu
A154 | 150 | 2" | 2" | 4 | #3/0 Al | 155 | 1 | #6 Cu
A204 | 200 | 2" | 2-1/2" | 4 | 250 Al | 205 | 1 | #6 Cu
A204E | 200 | 2" | 2" | 4 | #4/0 Al | 180 | 1 | #6 Cu | NEC 240-3 Exception #1
A404 | 400 | (2) 2" | (2) 2-1/2" | 8 | 250 Al | 410 | 2 | #2 Cu
A404E | 400 | 3-1/2" | 3-1/2" | 4 | 750 Al | 385 | 1 | #2 Cu | NEC 240-3 Exception #1
C64 | 60 | 1" | 1-1/4" | 4 | #4 Cu | 70 | 1 | #10 Cu
C104 | 100 | 1-1/2"' | 1-1/2"' | 4 | #1 Cu | 110 | 1 | #8 Cu
C154 | 150 | 1-1/2" | 1-1/2" | 4 | #1/0 Cu | 150 | 1 | #6 Cu
C204 | 200 | 2" | 2" | 4 | #3/0 Cu | 200 | 1 | #6 Cu
C404 | 400 | (2) 2" | (2) 2" | 8 | #3/0 Cu | 400 | 2 | #2 Cu
C404E | 400 | 3" | 3-1/2" | 4 | 500 MCM Cu | 380 | 1 | #2 Cu | NEC 240-3 Exception #1
C33T | 30 | - | 3/4" | 3 | #10 Cu | 30 | 1 | #8 Cu | Ground sized for 15 KVA Transformer
C53T | 50 | - | 3/4" | 3 | #6 Cu | 55 | 1 | #8 Cu | Ground sized for 30 KVA Transformer
C73T | 70 | - | 1" | 3 | #4 Cu | 70 | 1 | #4 Cu | Ground sized for 45 KVA Transformer
C103T | 100 | - | 1-1/4" | 3 | #1 Cu | 110 | 1 | #2 Cu | Ground sized for 75KVA Transformer
C173T | 175 | - | 2" | 3 | #2/0 Cu | 175 | 1 | #1/0 Cu | Ground sized for 112.5KVA Transformer
A103T | 100 | - | 1-1/2"' | 3 | #1/0 Al | 100 | 1 | #2 Cu | Ground sized for 75KVA transformer
FEEDER SCHEDULE - 3 Ph 4 W COMPACT Aluminum XHHW
***COMPACT ALUMINUM***
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity | (PVC or Flex ONLY)
A104 | 100 | #REF! | 1-1/2" | 4 | #1/0 Al | 100 | 1 | #8 Cu
A124 | 125 | 1-1/2" | 1-1/2" | 4 | #2/0 Al | 135 | 1 | #6 Cu
A154 | 150 | 2" | 2" | 4 | #3/0 Al | 155 | 1 | #6 Cu
A174 | 175 | 2" | 2" | 4 | #4/0 Al | 180 | 1 | #6 Cu
A204 | 200 | 2" | 2-1/2" | 4 | 250 Al | 205 | 1 | #6 Cu
A204E | 200 | 2" | 2" | 4 | #4/0 Al | 180 | 1 | #6 Cu | NEC 240-3 Exception #1
A224 | 225 | 2-1/2" | 2-1/2" | 4 | 300 Al | 230 | 1 | #4 Cu
A254 | 250 | 2-1/2" | 2-1/2" | 4 | 350 Al | 250 | 1 | #4 Cu
A304 | 300 | 3" | 3" | 4 | 500 Al | 310 | 1 | #4 Cu
A354 | 350 | 3-1/2" | 3-1/2" | 4 | 600 Al | 340 | 1 | #2 Cu
A404 | 400 | (2) 2" | (2) 2-1/2" | 8 | 250 Al | 410 | 2 | #2 Cu
A404E | 400 | 3-1/2" | 3-1/2" | 4 | 750 Al | 385 | 1 | #2 Cu | NEC 240-3 Exception #1
A504 | 500 | (2) 2-1/2" | (2) 3" | 8 | 350 Al | 500 | 2 | #1/0 Al
A604 | 600 | (2) 3" | (2) 3" | 8 | 500 Al | 620 | 2 | #2/0 Al
A804 | 800 | (3) 3" | (3) 3" | 12 | 400 Al | 810 | 3 | #3/0 Al
A804E | 800 | (3) 2-1/2" | (3) 3" | 12 | 350 Al | 750 | 3 | #3/0 Al | NEC 240-3 Exception #1
A1004 | 1000 | (3) 3-1/2" | (3) 3-1/2" | 12 | 600 Al | 1020 | 3 | #4/0 Al
A1204 | 1200 | (4) 3" | (4) 3" | 16 | 500 Al | 1240 | 4 | 250MCM Al
A1604 | 1600 | (5) 3-1/2" | (5) 3-1/2" | 20 | 600 Al | 1700 | 5 | 350MCM Al
A2004 | 2000 | (6) 3-1/2" | (6)3-1/2" | 24 | 600 Al | 2040 | 6 | 400MCM Al
A2504 | 2500 | (7) 3-1/2" | (7) 4" | 28 | 700 Al | 2625 | 7 | 600MCM Al
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "A404" shown on drawing - contractor can use "A404A" instead)
FEEDER SCHEDULE - 3 Ph 4 W Compact Aluminum XHHW 150% Neutral
(Neutral size is based on secondary transformer FLA x 150% instead of typical 125%)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
A104TN | 100 | 1-1/4" | 1-1/2" | 3 | #1/0 Al | 1 | #2/0 Al |  | 1 | #8 Cu | 30KVA
A154TN | 150 | 2" | 2" | 3 | #3/0 Al | 1 | 250 MCM Al |  | 1 | #6 Cu | 45KVA
A204TN | 200 | 2-1/2" | 2-1/2" | 3 | 250 MCM Al | 1 | 500 MCM Al |  | 1 | #6 Cu | 75KVA
A224TN | 225 | 3" | 3" | 3 | 300 MCM Al | 1 | 500 MCM Al |  | 1 | #4 Cu | 75KVA
A404TN | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | 250 MCM Al | 2 | 350 MCM Al |  | 2 | #2 Cu | 112.5KVA
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "A804N" shown on drawing - contractor can use "A804NA" instead)
FEEDER SCHEDULE - 3 Ph 4 W Compact Aluminum XHHW 150% Neutral
(Neutral size is Sized at 1.5 times)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
A204N | 205 | 2-1/2" | 2-1/2" | 3 | 250 MCM Al | 2 | #3/0 Al |  | 1 | #6 Cu
A224N | 225 | 2-1/2" | 2-1/2" | 3 | 300 MCM Al | 2 | #4/0 Al |  | 1 | #4 Cu
A404N | 410 | (2) 2-1/2" | (2) 2-1/2" | 6 | #250 MCM Al | 2 | 500 MCM Al |  | 2 | #2 Cu
A404EN | 360 | (2) 2" | (2) 2-1/2" | 6 | #4/0 Al | 2 | 400 MCM Al |  | 2 | #2 Cu | NEC 240-3 Exception #1
A1604N | 1600 | (5) 3-1/2" | (5) 3-1/2" | 15 | 600 MCM Al | 10 | 350 MCM Al |  | 5 | 350 MCM Al
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "A804N" shown on drawing - contractor can use "A804NA" instead)
FEEDER SCHEDULE - 3 Ph 4 W Compact Aluminum XHHW 200% Neutral
(Neutral size is Double Sized)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
A224NN | 225 | 3" | 3" | 3 | #300 MCM Al | 2 | #300MCM Al |  | 1 | #4 Cu
A404NN | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | #250 MCM Al | 4 | #250MCM Al |  | 2 | #2 Cu
A404ENN | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | #4/0 Al | 4 | #4/0 Al |  | 2 | #2 Cu | NEC 240-3 Exception #1
A1604NN | 1600 | (5) 3-1/2" | (5) 3-1/2" | 15 | #600 MCM Al | 10 | #500MCM Al |  | 5 | #350 MCM Al
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "A804N" shown on drawing - contractor can use "A804NA" instead)
¦::
FEEDER SCHEDULE - 3 Ph 3 W Compact Aluminum XHHW
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity | (PVC or Flex ONLY)
A103 | 100 | 1-1/4" | 1-1/2" | 3 | #1/0 Al | 100 | 1 | #8 Cu
A103T | 100 | - | 1-1/2"' | 3 | #1/0 Al | 100 | 1 | #2 Cu | Oversized ground for 75KVA transformer
A123 | 125 | 1-1/4" | 1-1/2" | 3 | #2/0 Al | 135 | 1 | #6 Cu
A153 | 150 | 1-1/2" | 1-1/2" | 3 | #3/0 Al | 155 | 1 | #6 Cu
A173 | 175 | 2" | 2" | 3 | #4/0 Al | 180 | 1 | #6 Cu
A173T | 175 | - | 2" | 3 | #4/0 Al | 180 | 1 | #3/0 Al | Oversized ground for 112.5KVA transformer
A203 | 200 | 2" | 2" | 3 | 250 Al | 205 | 1 | #6 Cu
A203E | 200 | 2" | 2" | 3 | #4/0 Al | 180 | 1 | #6 Cu | NEC 240-3 Exception #1
A223 | 225 | 2" | 2" | 3 | 300 Al | 230 | 1 | #4 Cu
A253 | 250 | 2" | 2-1/2" | 3 | 350 Al | 250 | 1 | #4 Cu
A303 | 300 | 2-1/2" | 2-1/2" | 3 | 500 Al | 310 | 1 | #4 Cu
A353 | 350 | 3" | 3" | 3 | 600 Al | 340 | 1 | #2 Cu
A403 | 400 | (2) 2" | (2) 2" | 6 | 250 Al | 410 | 2 | #2 Cu
A403E | 400 | 3" | 3" | 3 | 750 Al | 385 | 1 | #2 Cu | NEC 240-3 Exception #1
A503 | 500 | (2) 2" | (2) 2-1/2" | 6 | 350 Al | 500 | 2 | #1/0 Al
A603 | 600 | (2) 2-1/2" | (2) 3" | 6 | 500 Al | 620 | 2 | #2/0 Al
A803 | 800 | (3) 2-1/2" | (3) 2-1/2" | 9 | 400 Al | 810 | 3 | #3/0 Al
A803E | 800 | (3) 2" | (3) 2-1/2" | 9 | 350 Al | 750 | 3 | #3/0 Al | NEC 240-3 Exception #1
A1003 | 1000 | (3) 3" | (3) 3" | 9 | 600 Al | 1020 | 3 | #4/0 Al
A1203 | 1200 | (4) 2-1/2" | (4) 3" | 12 | 500 Al | 1240 | 4 | 250MCM Al
A1603 | 1600 | (5) 3" | (5) 3" | 15 | 600 Al | 1700 | 5 | 350MCM Al
A2003 | 2000 | (6) 3" | (6) 3" | 18 | 600 Al | 2040 | 6 | 400MCM Al
A2503 | 2500 | (7) 3" | (7) 3-1/2" | 21 | 700 Al | 2625 | 7 | 600MCM Al
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "A403" shown on drawing - contractor can use "A403A" instead)
¦::
FEEDER SCHEDULE - 3 Ph 4 W Copper THHN
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity | (PVC or Flex ONLY)
C34 | 30 | 3/4" | 3/4" | 4 | #10 Cu | 30 | 1 | #10 Cu
C44 | 40 | 3/4" | 3/4" | 4 | #8 Cu | 40 | 1 | #10 Cu
C54 | 50 | 3/4" | 1" | 4 | #6 Cu | 55 | 1 | #10 Cu
C64 | 60 | 1" | 1-1/4" | 4 | #4 Cu | 70 | 1 | #10 Cu
C74 | 70 | 1" | 1-1/4" | 4 | #4 Cu | 70 | 1 | #8 Cu
C84 | 80 | 1-1/4" | 1-1/4" | 4 | #2 Cu | 95 | 1 | #8 Cu
C94 | 90 | 1-1/4" | 1-1/4" | 4 | #2 Cu | 95 | 1 | #8 Cu
C104 | 100 | 1-1/2"' | 1-1/2" | 4 | #1 Cu | 110 | 1 | #8 Cu
C124 | 125 | 1-1/2" | 1-1/2" | 4 | #1 Cu | 130 | 1 | #6 Cu
C154 | 150 | 1-1/2" | 1-1/2" | 4 | #1/0 Cu | 150 | 1 | #6 Cu
C174 | 175 | 2" | 2" | 4 | #2/0 Cu | 175 | 1 | #6 Cu
C204 | 200 | 2" | 2" | 4 | #3/0 Cu | 200 | 1 | #6 Cu
C224 | 225 | 2" | 2-1/2" | 4 | #4/0 Cu | 230 | 1 | #4 Cu
C254 | 250 | 2-1/2" | 2-1/2" | 4 | 250 MCM Cu | 255 | 1 | #4 Cu
C304 | 300 | 2-1/2" | 3" | 4 | 300 MCM Cu | 285 | 1 | #4 Cu
C354 | 350 | 3" | 3" | 4 | 400 MCM Cu | 335 | 1 | #2 Cu
C404 | 400 | (2) 2" | (2) 2" | 8 | #3/0 Cu | 400 | 2 | #2 Cu
C404E | 400 | 3" | 3-1/2" | 4 | 500 MCM Cu | 380 | 1 | #2 Cu | NEC 240-3 Exception #1
C504 | 500 | 4" | 4" | 4 | 750 MCM Cu | 475 | 1 | #2 Cu
C604 | 600 | (2) 3" | (2) 3" | 8 | 350 MCM Cu | 620 | 2 | #1 Cu
C804 | 800 | (2) 3-1/2" | (2) 3-1/2" | 8 | 600 MCM Cu | 840 | 2 | #1/0 Cu
C804E | 800 | (2) 3" | (2) 3-1/2" | 8 | 500 MCM Cu | 760 | 2 | #1/0 Cu | NEC 240-3 Exception #1
C1004 | 1000 | (3) 3" | (3) 3" | 12 | 400 MCM Cu | 1005 | 3 | #2/0 Cu
C1204 | 1200 | (3) 3-1/2" | (3) 3-1/2" | 12 | 600 MCM Cu | 1260 | 3 | #3/0 Cu
C1604 | 1600 | (4) 3-1/2" | (4) 3-1/2" | 16 | 600 MCM Cu | 1680 | 4 | #4/0 Cu
C1604A | 1600 | (5) 3" | (5) 3" | 20 | 400 MCM Cu | 1675 | 5 | #4/0 Cu
C2004 | 2000 | (5) 3-1/2" | (5) 3-1/2" | 20 | 600 MCM Cu | 2100 | 5 | 250 MCM Cu
C2004A | 2000 | (6) 3" | (6) 3" | 24 | 400 MCM Cu | 2010 | 6 | 250 MCM Cu
C2504 | 2500 | (6) 3-1/2" | (6) 4" | 24 | 600 MCM Cu | 2520 | 6 | 350 MCM Cu
C2504A | 2500 | (7) 3" | (7) 3-1/2" | 28 | 500 MCM Cu | 2695 | 7 | 350 MCM Cu
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "C2504" shown on drawing - contractor can use "C2505A" instead)
FEEDER SCHEDULE - 3 Ph 4 W Copper THHN 150% Neutral
(Neutral size is based on secondary transformer FLA x 150% instead of typical 125%)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
C54TN | 50 | 1" | 1" | 3 | #6 Cu | 1 | #6 Cu |  | 1 | #10 Cu | 15KVA
C104TN | 100 | 1-1/2"' | 1-1/2" | 3 | #1 Cu | 1 | #1 Cu |  | 1 | # 8 Cu | 30KVA
C154TN | 150 | 2" | 2" | 3 | #1/0 Cu | 1 | #3/0 Cu |  | 1 | # 6 Cu | 45KVA
C204TN | 200 | 2-1/2" | 2-1/2" | 3 | #3/0 Cu | 1 | 350 MCM Cu |  | 1 | # 6 Cu | 75KVA
C224TN | 225 | 2-1/2" | 2-1/2" | 3 | #4/0 Cu | 1 | 350 MCM Cu |  | 1 | # 4 Cu | 75KVA
C404TN | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | #3/0 Cu | 2 | 250 MCM Cu |  | 2 | # 2 Cu | 112.5KVA
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "C804N" shown on drawing - contractor can use "C804NA" instead)
FEEDER SCHEDULE - 3 Ph 4 W Copper THHN 150% Neutral
(Neutral size is Sized at 1.5 times)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
C404N | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | #3/0 Cu | 2 | 350 MCM Cu |  | 2 | #2 Cu
¦::
FEEDER SCHEDULE - 3 Ph 3 W Copper THHN
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity | (PVC or Flex ONLY)
C33 | 30 | 3/4" | 3/4" | 3 | #10 Cu | 30 | 1 | #10 Cu
C33T | 30 | - | 3/4" | 3 | #10 Cu | 30 | 1 | #8 Cu | Ground sized for 15 KVA Transformer
C43 | 40 | 3/4" | 3/4" | 3 | #8 Cu | 40 | 1 | #10 Cu
C53 | 50 | 3/4" | 3/4" | 3 | #6 Cu | 55 | 1 | #10 Cu
C53T | 50 | - | 3/4" | 3 | #6 Cu | 55 | 1 | #8 Cu | Ground sized for 30 KVA Transformer
C63 | 60 | 1" | 1" | 3 | #4 Cu | 70 | 1 | #10 Cu
C73 | 70 | 1" | 1" | 3 | #4 Cu | 70 | 1 | #8 Cu
C73T | 70 | - | 1" | 3 | #4 Cu | 70 | 1 | #4 Cu | Ground sized for 45 KVA Transformer
C83 | 80 | 1-1/4" | 1-1/4" | 3 | #2 Cu | 95 | 1 | #8 Cu
C93 | 90 | 1-1/4" | 1-1/4" | 3 | #2 Cu | 95 | 1 | #8 Cu
C103 | 100 | 1-1/4" | 1-1/4" | 3 | #1 Cu | 110 | 1 | #8 Cu
C103T | 100 | - | 1-1/4" | 3 | #1 Cu | 110 | 1 | #2 Cu | Ground sized for 75KVA Transformer
C123 | 125 | 1-1/4" | 1-1/4" | 3 | #1 Cu | 130 | 1 | #6 Cu
C153 | 150 | 1-1/4" | 1-1/2" | 3 | #1/0 Cu | 150 | 1 | #6 Cu
C173 | 175 | 1-1/2" | 1-1/2" | 3 | #2/0 Cu | 175 | 1 | #6 Cu
C173T | 175 | - | 2" | 3 | #2/0 Cu | 175 | 1 | #1/0 Cu | Ground sized for 112.5KVA Transformer
C203 | 200 | 1-1/2" | 2" | 3 | #3/0 Cu | 200 | 1 | #6 Cu
C223 | 225 | 2" | 2" | 3 | #4/0 Cu | 230 | 1 | #4 Cu
C253 | 250 | 2" | 2" | 3 | 250 MCM Cu | 255 | 1 | #4 Cu
C303 | 300 | 2-1/2" | 2-1/2" | 3 | 300 MCM Cu | 285 | 1 | #4 Cu
C353 | 350 | 2-1/2" | 2-1/2" | 3 | 400 MCM Cu | 335 | 1 | #2 Cu
C403 | 400 | (2) 1-1/2" | (2) 2" | 6 | #3/0 Cu | 400 | 2 | #2 Cu
C403E | 400 | 3" | 3" | 3 | 500 MCM Cu | 380 | 1 | #2 Cu | NEC 240-3 Exception #1
C503 | 500 | 3-1/2" | 3-1/2" | 3 | 750 MCM Cu | 475 | 1 | #2 Cu
C603 | 600 | (2) 2-1/2" | (2) 2-1/2" | 6 | 350 MCM Cu | 620 | 2 | #1 Cu
C803 | 800 | (2) 3" | (2) 3" | 6 | 600 MCM Cu | 840 | 2 | #1/0 Cu
C1003 | 1000 | (3) 2-1/2" | (3) 3" | 9 | 400 MCM Cu | 1005 | 3 | #2/0 Cu
C1203 | 1200 | (3) 3" | (3) 3" | 9 | 600 MCM Cu | 1260 | 3 | #3/0 Cu
C1603 | 1600 | (4) 3" | (4) 3-1/2" | 12 | 600 MCM Cu | 1680 | 4 | #4/0 Cu
C1603A | 1600 | (5) 2-1/2" | (5) 3 | 15 | 400 MCM Cu | 1675 | 5 | #4/0 Cu
C2003 | 2000 | (5) 3" | (5) 3-1/2" | 15 | 600 MCM Cu | 2100 | 5 | 250 MCM Cu
C2003A | 2000 | (6) 2-1/2" | (6) 3" | 18 | 400 MCM Cu | 2010 | 6 | 250 MCM Cu
C2503 | 2500 | (6) 3" | (6) 3-1/2" | 18 | 600 MCM Cu | 2520 | 6 | 350 MCM Cu
C2503A | 2500 | (7) 3" | (7) 3" | 21 | 500 MCM Cu | 2660 | 7 | 350 MCM Cu
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "C2503" shown on drawing - contractor can use "C2503A" instead)
FEEDER SCHEDULE - 3 Ph 4 W Copper THHN 200% Neutral
(Neutral size is based on secondary transformer FLA x 200% instead of typical 125%)
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | NEUTRAL |  |  | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | QTY | SIZE |  | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) | [5 empty] | (PVC or Flex ONLY)
C104NN | 100 | 1-1/2" | 1-1/2" | 3 | #1 Cu | 1 | #2/0 Cu |  | 1 | # 8 Cu | 30KVA
C154NN | 150 | 2" | 2" | 3 | #1/0 Cu | 1 | 250 MCM Cu |  | 1 | # 6 Cu | 45 KVA
C224NN | 225 | 3" | 3" | 3 | #4/0 Cu | 1 | 600 MCM Cu |  | 1 | # 4 Cu | 75 KVA
C224NNA | 225 | (2) 1-1/2" | (2) 1-1/2" | 6 | #2 Cu | 2 | #4/0 Cu |  | 2 | # 4 Cu | 75 KVA
C404NN | 400 | (2) 2-1/2" | (2) 2-1/2" | 6 | #3/0 Cu | 2 | 350 MCM Cu |  | 2 | # 2 Cu | 112.5 KVA
C404ENN | 380 | 3-1/2" | 3-1/2" | 3 | 500 MCM Cu | 2 | 350 MCM Cu |  | 1 | # 2 Cu | 112.5 KVA
"A" after feeder designation indicates contractor has option of using primary feeder or alternate "A" feeder
(example: "C224NNT" shown on drawing - contractor can use "C224NNTA" instead)
FEEDER SCHEDULE - 1 Ph 3 W Copper THHN
FEEDER | AMPERAGE | CONDUIT |  | WIRE |  | Actual | GROUND (NEC 250-95)
NUMBER |  | EMT | PVC or Flex | QTY | SIZE | Wire | QTY | SIZE (Minimum)
|  | (No Gnd) | (W/Gnd) |  |  | Ampacity | (PVC or Flex ONLY)
C42T | 40 | - | 3/4" | 2 | #8 Cu | 50 | 1 | #8 Cu | Ground sized for 15 KVA 1 ph Transformer
C52 | 50 | 3/4" | 3/4" | 2 | #8 Cu | 50 | 1 | #10 Cu
BUS DUCT SCHEDULE - 3 Ph 4 W
FEEDER | AMPERAGE
NUMBER
BUS804 | 800
BUS1004 | 1000
BUS1204 | 1200
BUS1604 | 1600
BUS2004 | 2000
BUS DUCT SCHEDULE - 3 Ph 3 W
FEEDER | AMPERAGE
NUMBER
BUS803 | 800
BUS1003 | 1000
BUS1203 | 1200
BUS1603 | 1600
BUS2003 | 2000

## DwgList
ELECTRICAL DRAWING LIST FOR:
SHELL PERMIT
1 | E0.1 | 1-LINE, SYMBOL LIST
2 | E1.0 | SITE PLAN
3 | E1.1 | PHOTOMETRIC PLAN
4 | E2.0 | POWER PLAN
5 | E4.0 | PANEL SCHEDULES
6 | E5.0 | SCHEMATICS
7 | E5.1 | DETAILS
ELECTRICAL DRAWING LIST FOR:
TENANT IMPROVEMENT
1 | E0.1 | 1-LINE, SYMBOL LIST
2 | E0.2 | FIXTURE SCHEDULE
3 | E1.0 | SITE PLAN
4 | E1.1 | SITE PHOTOMETRIC PLAN
5 | E2.0 | POWER PLAN WAREHOUSE AREA
6 | E2.1 | POWER PLAN OFFICE AREAS
7 | E2.2 | POWER PLAN ROOF
8 | E3.0 | LIGHTING PLAN WAREHOUSE AREA
9 | E3.1 | LIGHTING PLAN OFFICE AREAS
10 | E4.0 | PANEL SCHEDULES
11 | E5.0 | SCHEMATICS
12 | E5.1 | DETAILS

## Index (hidden)
Panel 1 | Panel 2 | Panel 3 | Panel 4 | Panel 5 | Panel 6 | Panel 7 | Panel 8 | Panel 9 | Panel 10 | Panel 11 | Panel 12 | Panel 13 | Panel 14 | Panel 15 | Panel 16 | Panel 17 | Panel 18 | Panel 19 | Panel 20 |  | FirePump
6 | 6 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Voltage
240 | 240 | 240 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | Volts
4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Bus
2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Main
1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | AIC
2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Mount
3 | 3 | 3 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | Pnl Type (Loadctr/panelbd etc).
3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Type 1/3R/12
Notes | bar: Panel 1 to Panel 20
3 | 1 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Poles (# of)
3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Phase
2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Fdr - EMT/PVC
1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Fdr - Copper Alum | 2
13 | 7 | 15 | 15 | 15 | 15 | 7 | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 11 | 15 | 15 | 15 | 15 | Fdr - Wire Size | 21

## Stinger Leg
SMUD Stinger Leg
Smud feeds building with stinger on phase "C"
After main breaker, city and county and NEC want us to change phase C to phase B
At panel stinger leg is phase "B"
NEC 215-8 stinger leg to be phase taped "orange"
Ref NEC 215-8 384-3(e) 230-56
PG&E Stinger Leg
We think but have not confirmed that PG&E stinger leg is phase "B"

## Load FLA
| NamePlate | Stable Load | Peak Load
19" Monitor 5/2000 | 1.8A | 0.7A | 1.8A
350Mhz PC | 200W | 0.5A | 0.7A
Small UPS for PC | N/A | 0.0A | 0.1A
HP Laser Jet 4 | 6.4A | 4.0A | 5.5A | Recommend using 5.0A for load

## Harmonics (hidden)
INPUT
31232 | Watts Load Loss at 170 degrees C
12000 | Volts HV Winding LL (Delta Assumed)
3.815 | Ohms Resistance HV Winding*
480 | Volts LV Winding LL
0.00411 | Ohms Resistance LV Winding*
2500 | kVA Capacity 3 phase 150 deg C rise
h | I h (pu)
1 | 1 |  | 41.9
2 | 0.21332 |  | 8.938
3 | 0.0038234 |  | 0.1602
4 | 0.032291 |  | 1.353
5 | 0.13494 |  | 5.654
6 | 0.0011613 |  | 0.04866
7 | 0.022742 |  | 0.9529
8 | 0.027637 |  | 1.158
9 | 0.0033938 |  | 0.1422
10 | 0.006253 |  | 0.262
11 | 0.0479 |  | 2.007
12 | 0.0051671 |  | 0.2165
13 | 0.013766 |  | 0.5768
14 | 0.0093365 |  | 0.3912
15 | 0.0030907 |  | 0.1295
16 | 0 |  | 0
17 | 0 |  | 0
18 | 0 |  | 0
19 | 0 |  | 0
* Resistances are the sum of the three phases in series
0.84778 | R1 (HV Resistance) Delta Winding 2/9 of 3 phase resistance
0.00091333 | R2 (LV Resistance) Wye Winding 2/3 of 3 phase resistance CHANGE TO 2/3 IS 2/9 NOW!!!
120.2848 | I1
3007.1209 | I2
444.3624 | Pecr Watts (Winding Eddy Current Losses Under Rated Conditions)
0.10043 | Max Pecr (pu)
h | Ih (pu) | Ih (pu)^2 | h^2 | Ih(pu)^2 * h^2 | fh | fh^2 | fh^2 * h^2
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 0.21332 | 0.045504 | 4 | 0.18202 | 0.21332 | 0.045504 | 0.18202
3 | 0.0038234 | 1.4618e-05 | 9 | 0.00013156 | 0.0038234 | 1.4618e-05 | 0.00013156
4 | 0.032291 | 0.0010427 | 16 | 0.016684 | 0.032291 | 0.0010427 | 0.016684
5 | 0.13494 | 0.018209 | 25 | 0.45522 | 0.13494 | 0.018209 | 0.45522
6 | 0.0011613 | 1.3487e-06 | 36 | 4.8553e-05 | 0.0011613 | 1.3487e-06 | 4.8553e-05
7 | 0.022742 | 0.00051721 | 49 | 0.025343 | 0.022742 | 0.00051721 | 0.025343
8 | 0.027637 | 0.00076382 | 64 | 0.048884 | 0.027637 | 0.00076382 | 0.048884
9 | 0.0033938 | 1.1518e-05 | 81 | 0.00093295 | 0.0033938 | 1.1518e-05 | 0.00093295
10 | 0.006253 | 3.91e-05 | 100 | 0.00391 | 0.006253 | 3.91e-05 | 0.00391
11 | 0.0479 | 0.0022944 | 121 | 0.27762 | 0.0479 | 0.0022944 | 0.27762
12 | 0.0051671 | 2.6699e-05 | 144 | 0.0038446 | 0.0051671 | 2.6699e-05 | 0.0038446
13 | 0.013766 | 0.00018951 | 169 | 0.032026 | 0.013766 | 0.00018951 | 0.032026
14 | 0.0093365 | 8.7171e-05 | 196 | 0.017085 | 0.0093365 | 8.7171e-05 | 0.017085
15 | 0.0030907 | 9.5524e-06 | 225 | 0.0021493 | 0.0030907 | 9.5524e-06 | 0.0021493
16 | 0 | 0 | 256 | 0 | 0 | 0 | 0
17 | 0 | 0 | 289 | 0 | 0 | 0 | 0
18 | 0 | 0 | 324 | 0 | 0 | 0 | 0
19 | 0 | 0 | 361 | 0 | 0 | 0 | 0
| = | = | = | = | = | = | =
|  | 1.0687 |  | 2.0659 |  | 1.0687 | 2.0659
1.2762 | Pll (pu)
0.95996 | Imax (pu)
2886.7178 | Imax

## CoordStudy
WILLAMETTE
Electrical Power Study
Protective Device Coordination
Project: |  | Date:
Willamette |  | 2026-07-29 15:48
10268 Waterman Road
Elk Grove, CA 95624
Sacramento County
Project Summary:
Service Size: | 3,000 Amp
Service Voltage: | 277/480 Volt 3 Phase 4 Wire
Service Manufacturer: | Square "D"
Mark III References:
Archives Number: | 973069
Job Number: | 6631JG
Project Principal: | Jim Alexander
Electrical PM: | John Galliani
Prepared by :
Mark III Engineering Contractors
Fred Callison, P.E.
Table of Contents
1) Executive Summary
2) Recommendations
3) Table of Recommended Settings
4) Time Current Trip Curves

## CoordSturdy2
Executive Summary
Mark III Engineering Contractors was contracted as the design/build contractor for the Willamette Cardboard Manufacturing Plant in Elk Grove, California. As part of the design process, this coordination study is provided. This study is limited to settings for the 3,000 amp main circuit breaker in the electrical service and is based upon the single line as prepared by Mark III Engineering Contractors dated 10-9-98.
The goal of the settings is to reach a compromise between providing service continuity and equipment protection. In reaching this compromise, the consequences of service interruption and delay in clearing a fault must be considered.
Where possible, the settings should allow the lowest level breaker to clear the fault without upstream breakers tripping. This provides for minimum interruption to the facility equipment and is termed "selectivity".
The recommended settings are listed in section 3 of this study. Coordination between main service entrance breaker and breakers in main switchboard (KC200, KC225, LC400, LC600, MH800 and NA1200) were taken into consideration in this study.
A desirable level of selectivity was achieved for the system. An alternate setting recommendation has been provided for ground fault settings which, if implemented, will reduce the likihood of a service interruption under ground fault conditions.
Recommendations
1 | Protective devices should be set to values indicated in the attached table.
2 | Verify proper operation of ground fault system.
3 | This coordination study should be updated whenever significant changes to the system are made such as:
a) Addition of loads to the system
b) Addition of circuits to the system
c) Replacement of conductors with larger or different insulation/type conductors
d) Replacement of transformers with different impedance or size

## CoordStudy3
Recommended Settings - Willamette Elk Grove CA
Square "D"
MSB | SE3000 | Rating Plug RP100
Rating Plug: |  | 3000A
| Type: | RP100
Long Time |  |  | Amps
| Pickup: | 1.0 | 3000
| Delay: | 11
Short Time
| Pickup: | 6.0
| Delay: | 0.5
Instant: |  | 5.0 | 15000
Ground Fault
| Amps: | 800 | 800
| Delay: | 0.1 I2 IN
| Alarm: | 640 | 640
Alternate Settings - Willamette Elk Grove CA
If a pilot light and alarm bell connected to the ground fault alarm are installed in
the main switchboard room (or preferably in the maintenance office), the following
alternate settings are recommended. These settings reduce the probability of
service interruption on ground fault by providing a warning to maintenance
personnel under certain conditions.
Square "D"
MSB | SE3000 | Rating Plug RP100
Rating Plug: |  | 3000A
| Type: | RP100
Long Time |  |  | Amps
| Pickup: | 1.0 | 3000
| Delay: | 11
Short Time
| Pickup: | 6.0
| Delay: | 0.5
Instant: |  | 5.0 | 15000
Ground Fault
| Amps: | 1200 | 1200
| Delay: | 0.1 I2 IN
| Alarm: | 640 | 640

## Motor Fdr Calcs
Iceland
|  | Unit | Fuse
Unit | Full Load Calculations | FLA | Size
AC-4 | Unit MCA = 53A | 49 | 70
Largest Motor Load = 16A
FLA = MCA - (25% of Largest Motor)
FLA = 53 - (0.25 * 16) = 49 Amps
AC-6 | Unit MCA = 49 | 45 | 60
Largest Motor Load = 16A
FLA = 49 - (0.25 * 16) = 45 Amps
AC-8 | Unit MCA = 49 | 45 | 60
Largest Motor Load = 16A
FLA = 49 - (0.25 * 16) = 45 Amps
AC-10 | Unit MCA = 55 | 50 | 60
Largest Motor Load = 19A
FLA = 55 - (0.25 * 19) = 50 Amps
Feeder Conductor (NEC 430-24)
(Single largest motor x 1.25) + (sum of other motors)
AC-4 | 50 (Largest Motor 19FLA) | 50
AC-6 | 45 | 45
AC-8 | 45 | 45
AC-10 | 50 | 50
=====
| 25% of Single Largest Motor | 4.75
| Feeder MCA | 194.75 | Amps
Feeder Short Circuit and Ground Fault Protection (NEC 430-62) and (NEC 240-6A)
Maximum size = (Single largest protective device) + (sum of other motor FLA's)
AC-4 | Largest Protective Device 70A | 70
AC-6 | 45 | 45
AC-8 | 45 | 45
AC-10 | 50 | 50
=====
| Protection can not be greater than: | 210 | Amps
| Next size down per NEC 240-6A: | 200 | Amps
Use 200A Circuit Breaker with minimum 195 amp wire.

## PC Loads
[6 empty] | Single Phase Amps @120V |  |  |  | kVA @120/208V 3 Ph |  |  |  | 120/208V 3 Ph Amps
[6 empty] | Actual | Peak | Nameplate |  | Actual | Peak | Nameplate |  | Actual | Peak | Nameplate |  | Actual Amps (stable) |  |  |  | Peak Amps |  |  |  | Nameplate Amps
DESC | Stations | PC Boxes | 19" Monitors | HP Laser Jet 4 | [13 empty] | PC Box | Monitor | Laser |  | PC Box | Monitor | Laser |  | PC Box | Monitor | Laser
NOW | 200 | 200 | 200 | 25 |  | 380 | 635 | 740 |  | 45.6 | 76.2 | 88.8 |  | 126.6667 | 211.6667 | 246.6667 |  | 0.7 | 0.7 | 4 |  | 0.7 | 1.8 | 5.4 |  | 1.1 | 1.8 | 6.4
FUTURE | 50 | 50 | 50 | 10 |  | 110 | 179 | 209 |  | 13.2 | 21.48 | 25.08 |  | 36.6667 | 59.6667 | 69.6667 |  | 0.7 | 0.7 | 4 |  | 0.7 | 1.8 | 5.4 |  | 1.1 | 1.8 | 6.4
| = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
TOTAL | 250 | 250 | 250 | 35 |  | 490 | 814 | 949 |  | 58.8 | 97.68 | 113.88 |  | 163.3333 | 271.3333 | 316.3333 |  | 0.7 | 0.7 | 4 |  | 0.7 | 1.8 | 5.4 |  | 1.1 | 1.8 | 6.4

## KirkKey Procedures
SINGLE GENERATOR OPERATION
OVERVIEW
This procedure covers emergency shutdown steps should one of the two on-site generators fail to start.
BACKGROUND
This electrical system can be switched to feed distribution boards DB1 and DB2 from either generator.
Each generator is sized to feed most, if not all, the emergency loads in the building. Electrical loads must
be monitored after switching to ensure the generator does not stall. When the second generator comes
back on line or utility power is restored, the bus switches should be reset. This requires a short shutdown.
PROCEDURE TO TIE ALL EMERGENCY LOADS
TO ONE GENERATOR
Step 1: | NOTIFY EMERGENCY CREWS
Call Mark III emergency number: 916-381-8080
Page Ron Neese of Mark III at 916-731-9385
Call Sierra Generator 916-372-5078
Page Kris Choate of Mark III at 916-731-0734
Step 2: | SHED LOADS
Open the following breakers in DB1:
EHB
EH2
Open the following breakers in DB2:
GH9
GHB
Step 3: | DISCONNECT NON-OPERATIONAL GENERATOR
Open kirk key switch of non-operational generator.
(indicated by red light at DB2 panel)
Remove kirk key.
Step 4: | CONNECT LOADS TO OPERATIONAL GENERATOR
Insert kirk key in tie break switch.
Close kirk key tie break switch.
Step 5: | ADJUST GENERATOR LOADING
In the unlikely event the load is too high, open the following breakers in DB1
one at a time while monitoring the generator loading:
EH1: West High Bay Lights
EH3: Center High Bay Lights
EH4: Center High Bay Lights
If additional load can be added, close the following
breakers one at a time while monitoring generator loading:
DB1: EH2 - High Bay Lights Column 1 to 5 and misc. receptacles
DB1: EHB - Battery Chargers
DB2: GHB - Battery Chargers
DB2: GH9 - Warehouse Ventilation
Step 6: | MONITOR LOADING
Monitor generator loads to insure generator does not become overloaded.
PROCEDURE TO CONNECT EMERGENCY LOADS
BACK TO NORMAL CONFIGURATION
Step 1: | NOTIFY EXCEL SUPERVISORS
Explain that some electrical loads will be turning off for a short time.
Step 2: | VERIFY GENERATOR OR UTILITY POWER ON AND STABLE
Indicated by green lights at DB2.
Step 3: | DISCONNECT TIE BREAK (shuts power off at DB1 or DB2)
Open kirk key tie break switch.
Remove kirk key.
Step 4: | CONNECT LOAD NORMALLY
Insert kirk key in switch.
Close kirk key switch to distribution board
Step 5: | CLOSE OPENED BREAKERS
DB1: EH1: West High Bay Lights
DB1: EH3: Center High Bay Lights
DB1: EH4: Center High Bay Lights
DB1: EH2 - High Bay Lights Column 1 to 5 and misc. receptacles
DB1: EHB - Battery Chargers
DB2: GHB - Battery Chargers
DB2: GH9 - Warehouse Ventilation