Current status:

The City of Sacramento Building Department raised a significant concern about the fire protection level at the American Ice Building which is adjacent to the new Iceland improvements.  This has caused some delays while we figured out how to deal with it.  The current plan is to submit a separate, companion permit application for improvements at American Ice.  Both the American Ice permit and the Iceland permit will need to be completed before we will be able to open Iceland again.

The improvements at American Ice are minor.  The eave/overhang will be removed, the face recovered with non-combustible materials, and the inside roof edge covered with gypsum board.  I will handle these tasks and the permit application as an owner/builder.

1.  Part of existing building to be removed?  (red tag)

Yes, this will be removed by the owner as part of the American Ice improvements.

2.  Existing building overhang to be removed.  (red tag)

Yes, this will be removed by the owner as part of the American Ice improvements.

3.  Proposed additional storage area?  (dark blue tag)

Yes.  This is new area that will be under the new roof.  This existing area is about 18” below the finished floor for the rest of Iceland.  This area will need to be filled and a new concrete floor installed at the rink finished floor level.

4.  Grading for additional storage area? (dark blue tag)

The new finished floor in the storage area should be brought up to the rink finished floor level.

5.  Proposed double check valve... (orange tag)

Yes, the double check valve would be in the way of Zamboni operations here.  We need to find a different spot.

6.  Would double check valve work here? (orange tag)

It could work here but it would block off access to the area to the right on the drawing.  I don't know the rules on location of the check valve.  I surmise it needs to be near the property line, outside the building.  If my guess is correct, locating it as far to the right in that area as easily possible would be best since it would leave us the most flexibility in that area in the future.  I put an aqua asterisk on two possible locations.

7.  Civil to provide ADA path of travel to Del Paso R/W. (green tag)

This path is currently accessible.  No addition work is needed in this area.

8.  Fire riser room door may conflict with utility pole.

The utility poles and transformers have been removed from this area.

9.  Clouded area

The architect has raised an issue about exit travel paths.  He says that the distance to the accessible exits is too long from the back of the south side of the rink to the exits on the north and northwest sides of the rink.  He is examining options but feels that we may need to add an accessible exit on the southwest side of the rink near the Zamboni roll up door.